Date:	08/14/09
Vendor Name:		BACnet Stack hosted on SourceForge.net
Product Name:		BACnet Development Kit
Product Model Number:			bdk-atxx4-mstp
Applications Software Version:				1	Firmware Revision:	0.5.3
BACnet Protocol Revision:				5

Product Description:
Example BACnet MS/TP device used with the BACnet Stack hosted on SourceForge.net

BACnet Standardized Device Profile (Annex L)
	BACnet Operator Workstation (B-OWS)
	BACnet Building Controller (B-BC)
	BACnet Advanced Application Controller (B-AAC)
x	BACnet Application Specific Controller (B-ASC)
	BACnet Smart Sensor (B-SS)
	BACnet Smart Actuator (B-SA)

List all BACnet Interoperability Building Blocks supported (see Annex K in BACnet Addendum 135d):
DS-RP-B Read Property / DS-WP-B Write Property / DM-DDB-B Dynamic Device Binding / DM-DOB-B Dynamic Object Binding / DM-DCC-B Device Communication Control / DS-RPM-B ReadPropertyMultiple / DM-RD-B Reinitialize Device

Which of the following device binding methods does the product support? (check one or more)
	Send Who-Is, receive I-Am (BIBB DM-DDB-A)
x	Receive Who-Is, send I-Am (BIBB DM-DDB-B)
	Send Who-Has, receive I-Have (BIBB DM-DOB-A)
x	Receive Who-Has, send I-Have (BIBB DM-DOB-B)
	Manual configuration of recipient device's network number and MAC address
	None of the above

Standard Object Types Supported:

Analog Input Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard

	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

List of non-dynamic object identifiers and their meaning in this device
Object Identifier		Meaning
Analog Input 0		AVR ADC7 input
Analog Input 1		demo object - no meaning

Analog Value Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard
Present_Value
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

List of non-dynamic object identifiers and their meaning in this device
Object Identifier		Meaning
Analog Value 0		demo object - no meaning
Analog Value 1		demo object - no meaning
Analog Value 2		demo object - no meaning
Analog Value 3		demo object - no meaning

Binary Input Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description
	4. List of all properties that are writable where not otherwise required by this standard

	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

List of non-dynamic object identifiers and their meaning in this device
Object Identifier		Meaning
Binary Input 0		Pin PB0
Binary Input 1		Pin PB1
Binary Input 2		Pin PB2
Binary Input 3		Pin PB3
Binary Input 4		Pin PB4
Binary Input 5		demo object - no meaning
Binary Input 6		demo object - no meaning
Binary Input 7		demo object - no meaning

Binary Output Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description, Active_Text, Inactive_Text
	4. List of all properties that are writable where not otherwise required by this standard
Out_Of_Service, Polarity
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

List of non-dynamic object identifiers and their meaning in this device
Object Identifier		Meaning
Binary Output 0		LED 2
Binary Output 1		LED 3

Device Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:
Description, Protocol_Conformance_Class
	4. List of all properties that are writable where not otherwise required by this standard
Object_Name / Max_Master / Max_Info_Frames / Object_Identifier
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning
9600		Unsigned	Baud Rate (writable)
512		Unsigned	C-Stack Size
513		Unsigned	C-Stack Unused
	6. List of any property value range restrictions:
Property Identifier		Restrictions
Object_Name		< 32 bytes
Object_Identifier		Device Type only.
Number_Of_APDU_Retries		0-255
APDU_Timeout		0-65535 milliseconds
Vendor_Identifier		0-65535
System_Status

Data Link Layer Options (check all that are supported):

	BACnet IP, (Annex J)
	BACnet IP, (Annex J), Foreign Device
	ISO 8802-3, Ethernet (Clause 7)
	ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8)
	ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate(s):
X	MS/TP master (Clause 9), baud rate(s):	9600, 19200, 38400, 57600, 76800
	MS/TP slave (Clause 9), baud rate(s):
	Point-To-Point, EIA 232 (Clause 10), baud rate(s):
	Point-To-Point, modem, (Clause 10), baud rate(s):
	LonTalk, (Clause 11), medium:
	Other:

Networking Options (check all that are supported):

Router, Clause 6 - List all routing configurations (e.g. ARCNET-Ethernet, Ethernet-MS/TP, etc.):

Annex H.3, BACnet Tunneling Router over UDP/IP
BACnet/IP Broadcast Management Device (BBMD)
BBMD supports registrations by Foreign Devices

Segmentation Capability (check all that apply):
	Window Size
Segmented requests supported
Segmented responses supported

Character Sets Supported (check all that apply):
Indicating support for multiple character sets does not imply that they can all be supported simultaneously.

x	ANSI X3.4
	IBM/Microsoft DBCS
	ISO 8859-1
	ISO 10646 (UCS-2)
	ISO 10646 (ICS-4)
	JIS C 6226

If this product is a communication gateway, describe the non-BACnet equipment/network(s) that the gateway supports:
N/A

Include any addition information about the product's BACnet capabilities relevant to interoperability: